## OPERATIONAL COMPLIANCE
ASC OPERATIONAL COMPLIANCE CALENDAR
MONTHLY/QUARTERLY/ANNUAL AND VARIABLE REQUIREMENTS
|  |  | Q 1 |  |  | Q 2 |  |  | Q3 |  |  | Q4
REQUIREMENT | DOCUMENTATION | FREQUENCY | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | PSS P&P REFERENCE
State-mandated SSI (and other) Reporting | Report to NHSN: Colorado, Massachusetts, Nevada, New Hampshire, New Jersey, and Texas Requires reporting by ASCs using NHSN SSI definitions, but to their state-based database - Missouri Check your state regulations regarding additional state-mandated reporting. | D A/I/O | [12 empty] | QAPI section 5
Complete Crash Cart Inspection | Break lock and check every drawer for supplies per approved inventory. Replace expired supplies. | M | [12 empty] | Nursing section 4
Credentials Expiration Dates | Track expiration dates for physician credentials and facility staff licensure/certification, etc. Update expired documents and online verifications, as needed. | M | [12 empty] | Credentialing and Human Resources sections 1
Expired Medications Inspection | Dispose of all expired medications appropriately (28 days) throughtout the facility. Make sure open MDV are appropriately stored and labeled. | M | [12 empty] | Anesthesia/Medication Management section 2
Infection Control Query | Query physicians for procedures performed to identify postoperative infections or complications. Document peer review for reported infections/complications. Document infection investigation for postop infections. | M | [12 empty] | QAPI section 5
ASC-20 NHSN COVID-19 Vaccination Reporting | Report COVID-19 vaccination information to the NHSN monthly and by quarterly deadline. Track vaccination and booster information for staff. | M
Infection Control Compliance | Quarterly facility audit and report results to the QAPI Committee. | Q | [12 empty] | QAPI section 5
QAPI/Medical Advisory Committee/Governing Body Meeting | Meeting minutes. Follow format of initial sample meeting minutes | Q
Medical Records Audits | Random audit of medical records per facility policy. Report results to the QAPI Committee. | Q | [12 empty] | QAPI section 2
Peer Review | Random and incident based peer review per facility policy. (Quad A has specific forms for MDs/DOS and submission must be to Quad A – please refer to accreditation standards). | Q | [12 empty] | QAPI section 4
Pharmacy Inspection | By Consulting Pharmacist. Please note your state requirements may require more frequent pharmacy inspections. If your state does not require a pharmacy consultant, we recommend your pharmacy nurse designee perform this task at least quarterly. Report results to the QAPI Committee. | Q | [12 empty] | Anesthesia/Medication Management section 2
ASCQR Measures Reporting | Conduct annual ASCQR measures reporting per Specifications Manual by dealine. Measures change annually and may be claims or web-based measures. Deadlines are typically in May of each year but this is subject to change. Track identified web-based measures throughout the data collection period. This is typically Jan 1 through Dec 31. | A | bar: Q 2 MAY
Annual Review (TJC accredited only) | Evaluate and document the organization’s performance in relation to its mission, values and goals. Evaluate if the organization has developed a culture of safety and quality and identify changes required, based on this evaluation. Must address scope, objective, performance and effectiveness criteria. Present to MAC/GB with any suggestions of improvements and/or changes. | A
Benchmarking | At least one benchmarking activity annually. Reference industry literature, accreditation agencies and/or trade associations for benchmarking resources. | A
Disaster Preparedness Program Evaluation | Evaluate and document the effectiveness of program and present to MAC/GB with any suggestions of improvements and/or changes. | A | [12 empty] | Safety section 2 or 3 – Disaster Safety
Employee Competencies | Ensure didactic competencies are completed and include mandatory requirements such as OSHA, fire safety, disaster, infection control, pt. rights, etc. Perform and document observed employee competencies and include in appraisals/evaluations. | A | [12 empty] | Document as inservices – Human Resources section 1
Employee Performance Appraisals/Evaluations | Competency based, per employee’s job descriptions duties. | A | [12 empty] | Human Resources section 3
Governing Body Report (TJC accredited facilities only) | Provide the GB with a written report regarding the results of proactive risk assessments, lessons learned from root cause analyses, all systems or process failures, the number and type of sentinel events, whether patients and the families were informed of sentinel events and all actions taken to improve safety | A | [12 empty] | For TJC accredited facilities only
HIPAA Risk Assessment | Perform and document a HIPAA Risk Assessment. An outside expert is recommended. | A
Infection Control Risk Assessment | Prioritize infection control risks by conducting and documenting an Infection Control Risk Assessment. Report results to the QAPI Committee. | A | [12 empty] | Infection Control section 1
Infection Control Program Evaluation | Perform and document the effectiveness of the IC Program. This can be included in your QAPI Program Evaluation. | A | [12 empty] | QAPI section 1
Mock Code | Conduct a mock code. Include an evaluation with the report, including recommendations for improvement. | A | [12 empty] | Nursing section 4
Malignant Hyperthermia Code | Conduct a MH drill. Include an evaluation with the report, including recommendations for improvement. | A | [12 empty] | Document as inservice – Human Resources section 1
Policy and Procedures Review | Review P&Ps, edit/add/revise and document approval from MAC/GB meeting minutes. All Policy Adoption Pages should be dated and signed. Any polices that are revised or new should be date stamped. Document in meeting minutes. | A
QAPI Program Evaluation | Evaluate effectiveness of the QAPI Program. Include review of your measured indicators. | A | [12 empty] | QAPI section 1
Review and Evaluation of Contracted Services | Evaluate quality of all ancillary services. Present at MAC/GB meeting with recommendations for change/reapproval. Include GB action to change/reapprove in meeting minutes. | A | [12 empty] | QAPI section 2
TB Risk Assessment | CDC TB Risk Assessment to assure facility remains low risk, if applicable. All HCWs should complete annual TB questionnaire. | A | [12 empty] | Infection Control section 2
Controlled Substances Inventory | Consulting pharmacist inventory of all controlled substances (including drugs and quantities). Have consulting pharmacist document on their letterhead to make it official | 2Y
Medical Staff Recredentialing | Medical staff reappointment by the Governing Body (peer review should be part of reappointment process). Refer to Credentialing Guide for recredentialing process. Should be documented in meeting minutes. | 2Y | [12 empty] | Credentialing
Instrumentation | Ensure current directions for disinfection and sterilization of all instrumentation is available and that all manufacturer’s directions are being followed. | PMG
Sterilization Equipment and Supplies | Ensure current directions for use are available for staff to maintain equipment per manufacturer’s guidelines. This includes ultrasonic cleaners, sterilizers, washers, enzymatic cleaners, etc. | PMG
Patient Warming Device Filters | Depending on the model, filters need to be changed, every 500 hours or 6 months, or every 500 hours or 1 year. Check the manufacturer’s recommendations. Keep with contract for annual evaluation | PMG
Ice Machine Cleaning | Follow manufacturer’s guidelines for frequency and process. Document in a log | PMG
Refrigerator Cleaning | Follow manufacturer’s guidelines for frequency and process. | PMG | [12 empty] | Anesthesia/Medication Management section 2
Pregnancy Test Control Log | Follow manufacturer’s guidelines for frequency and process. | PMG | [12 empty] | Nursing section 1
Quality Control for Blood Glucose Testing | Follow manufacturer’s guidelines for how often to run and log controls. | PMG | [12 empty] | Nursing section 1
D I/A/O = Daily if applicable and/or with occurrence
M = Monthly
Q = Quarterly
A = Annual
2Y = Every 2 Years
PMG = Per Manufacturers Guidelines

## OPS DAILY REQUIREMENTS
ASC OPERATIONAL COMPLIANCE CALENDAR
DAILY REQUIREMENTS
REQUIREMENT | DOCUMENTATION | FREQUENCY | PSS P&P REFERENCE
Biological Indicator Test | Log for sterilizers in use. Track in a log book. Typically they come with indicator system. | D
Blanket and/or Fluid Warmer | Log temperature. Include acceptable range for per manufacturer DFUs for fluids stored, and action/resolution if temperature is out of range. | D | Nursing section 2
Bowie-Dick Test | Log for prevac sterilizers in use. Track in log book. | D | Infection Control section 1.
Controlled Substances Perpetual Inventory | Log opening and closing counts, additions/deletions to inventory, wasted drug quantities; Inventory counts and waste documentation require 2 RN signatures. | D | Anesthesia/Medication Management section 2
Controlled Substance Administration Sheet | Record of patient, medication, dose administered, and administered by. | D | Anesthesia/Medication Management section 2
Crash Cart Inspection | Log AED/Defibrillator test, external cart inspection including suction, oxygen supply, drug outdate list, etc. | D | Nursing section 4
Environmental Sanitation | Log daily housekeeping performed including terminal cleaning of operating /procedure rooms. | D | Infection Control section 1
Medication Lot Numbers | Log lot #s of all meds used in preop/PACU/OR in case of recall (OPTIONAL). Create daily log for lot #s of all medications used. In OR also document lot #s for other sterile items and equipment that may be part of an infection investigation. | D
Refrigerator Temperature | Log temperature using a 24/7 thermometer, including action and resolution if the temperature is out of range. Refrigerator range 36 – 46°F Freezer range 4 – 14°F (or manufacturers recommendations of frozen item). | D | Anesthesia/Medication Management section 2
Surgical Log | Log patient ID, date, procedure, physician, anesthesia type, at a minimum. May be electronic. | D | Refer to Nursing section 5 for data to include
Cidex OPA | Log patient ID, date, time, operator, items soaked, and monitoring strip results. | D I/A/O | Infection Control section 1
DEA 222 | Log upon receipt of controlled substances, per facility policy. | D I/A/O | Anesthesia/Medication Management section 2
Equipment Repair | Log equipment, malfunction description, date out, out to whom, date in. | D I/A/O | Safety section 4 or 5 – Equipment Safety
Exceptions | Track exceptions that do not rise to the severity of an incident to identify trends and take action as appropriate. | D I/A/O | QAPI section 3
IUSS Sterilization | Log patient ID, date/time, load #, items, cycle length, operator, chemical indicator, reason. (IUSS is reserved for specific circumstances and criteria). | D I/A/O | Infection Control section 1
Incident Report | Document description of occurrence (without opinion) and to whom/when it was reported so it can be investigated and analyzed. | D I/A/O | QAPI section 3
Incident Report Log | Log date, incident #, brief description and action taken. | D I/A/O | QAPI section 3
Infection Control Tracking Log (HFAP only) | Date, patient, procedure, condition of patients with increased risk for infection due to intravascular device, immunocompromised, medical instability, morbidly obese, etc. | D I/A/O | Infection Control section 1
Sharps Injury | Log sharps injury using approved facility sharps injury log form. | D I/A/O | OSHA section 2
Specimen/Tissue | Log at a minimum, date, patient name, diagnosis, requesting MD, tissue sent and verify path report received. | D I/A/O | Nursing section 2 / QAPI section 2
State-mandated SSI (and other) Reporting | Report to NHSN: Colorado, Massachusetts, Nevada, New Hampshire, New Jersey, and Texas Requires reporting by ASCs using NHSN SSI definitions, but to their state-based database - Missouri Check your state regulations regarding additional state-mandated reporting. | D A/I/O | QAPI section 5
D = Daily
D I/A/O = Daily if applicable and/or with occurrence

## LIFE SAFETY CODE COMPLIANCE
ASC LIFE SAFETY CODE COMPLIANCE CALENDAR
MONTHLY/QUARTERLY/ANNUAL AND VARIABLE REQUIREMENTS
|  |  |  | Q 1 |  |  | Q 2 |  |  | Q3 |  |  | Q4
REQUIREMENT | DOCUMENTATION | WHO IS RESPONSIBLE | FREQUENCY | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | PSS P&P REFERENCE
Emergency Generator Inspection | Verify enclosure is secure; area is clean, free of debris, and there are no conditions that can interfere with effective operation. Confer with vendor to determine additional observations that may be appropriate to document. Document training as an inservice and create log based on this training. | Trained Facility Personnel | W | [12 empty] | Safety section 3 or 4 – Safety Management
Sprinkler System | Visual inspections of the backflow valves, pressure-regulating devices pressures/no leaks, control valves in correct position and sealed. Document accordingly. | Trained Facility Personnel | W | [12 empty] | QAPI section 2 Safety section 3 or 4 - Safety Management
Eye Wash Station Inspection | Log weekly tests, per facility policy (pass or fail). | Trained Facility Personnel | W | [12 empty] | OSHA section 3
Physical Environment Checklist | Complete Physical Environment Checklist and report audit results to the QAPI Committee. | Trained Facility Personnel | M | [12 empty] | QAPI section 2
Directional Airflow Monitoring | Positive/negative air pressure testing (soiled utility/clean utility/OR/Procedure) including action and resolution if the air flow is not appropriate to the room. | Trained Facility Personnel & Vendor on an Annual Basis (T&B) | M | [12 empty] | Nursing section 2
Emergency Egress Lighting (Fire EXIT Signs) | Perform and document a functional test of all battery-powered lights required for egress for a minimum duration of 30 seconds. Ensure two bulbs per fixture are working. Create a log and keep documentation of this. | Trained Facility Personnel | M | [12 empty] | Safety section 2 - Disaster Safety
OR Emergency Lighting | Emergency lights are tested every month for 30 seconds to ensure they are in good working condition. Power needs to be shut off to the ASC and activate generator transfer switch. Make a check if they are in good working condition. Document accordingly on OR Emergency Lights Log. | Trained Facility Personnel | M | [12 empty] | Safety section 2 - Disaster Safety
Line Isolation Monitoring | If applicable. Perform or obtain testing report of monthly line isolation monitoring circuits. The system installer should instruct staff members how to conduct the testing. The test button must test both audio and visual alarms. If your system is self testing and self calibrating, document when the monthly self test is completed but conduct one manual test per year. | Facility Personnel for alarms on a montly basis - Annual test by Electrical Vendor | M | [12 empty] | Safety section 3 or 4 – Safety Management
Generator Load Test & Checks | Perform monthly load test. Fuel, cooling, lubricating, starting, and exhaust system checks, battery specific gravity or conductance testing (sealed battery), transfer switch and general system checks. Document load test and checks accordingly. Change oil and fuel filters every six months. | Trained Internal Personnel | M | [12 empty] | Safety section 3 or 4 – Safety Management
Fire Extinguisher Inspection | Log monthly visual inspection of the interior and external fire extinguishers. Turn extinguisher upside down three times. Log should include the date of the inspection and the initials of the inspector. | Trained Internal Personnel | M | [12 empty] | Safety section 1 - Fire Safety
GFCI Outlet Testing | Log completion on monthly Physical Environment Checklist. | Trained Internal Personnel | M | [12 empty] | QAPI section 2 Safety section 3 or 4 - Safety Management
Electrical Panels | Log completion on monthly Physical Environment Checklist. | Trained Internal Personnel | M | [12 empty] | QAPI section 2 Safety section 3 or 4 - Safety Management
ABHR Dispensers and Storage | Log completion on monthly Physical Environment Checklist. | Trained Internal Personnel | M | [12 empty] | QAPI section 2 Safety section 3 or 4 - Safety Management
Fire Doors | Log completion on monthly Physical Environment Checklist. | Trained Internal Personnel | M | [12 empty] | QAPI section 2 Safety section 3 or 4 - Safety Management
Visual Fire Sprinkler Test | Log completion on monthly Physical Environment Checklist. | Trained Internal Personnel | M | [12 empty] | QAPI section 2 Safety section 3 or 4 - Safety Management
Fire Drill | Conduct unannounced drill with automatic transmission of signal to the servicing fire department. Patients do not need to be evacuated, but all available staff should participate in an evacuation drill. | Trained Facility Personnel | Q | [12 empty] | Safety section 1 or 2 – Fire Safety
Disaster Drill | AAAHC - Scenario-based drills of the internal and external emergency and disaster preparedness plan are conducted quarterly with written evaluation (one with CPR and MH, as applicable). | Facility Personnel | Q
HVAC Inspection, Service, Filter Changes | Conduct quarterly inspection and service, per manufacturer recommendations. Obtain report from HVAC contractor. Maintain service report with contract for annual evaluation. | HVAC Vendor | Q
Environment of Care Risk Assessments | Conduct Hazard Vulnerability Analysis and Facility Building Category Risk Assessments and have QAPI/Governing Body/MAC review and approve. | Trained Facility Personnel | A | [12 empty] | Safety section 3 or 4 – Safety Management
Automatic Fire/Smoke Doors and Assemblies | Obtain reports for required ITMs from your ancillary contracted vendor. Keep with contract for annual evaluation. | Fire Door Assembly Vendor (Trained) | A
Emergency Preparedness Exercise | Conduct an exercise to test the emergency plan annually. Participate in a full-scale exercise that is community-based every 2 years. When a community-based exercise is not accessible, conduct a facility-based functional exercise every 2 years OR if you experiences an actual natural or man-made emergency that requires activation of the emergency plan, you are exempt from engaging in its next required exercise. Conduct an additional exercise at least every 2 years, opposite the year the full-scale or functional exercise. This may include a second full-scale exercise that is community-based or individual, facility-based functional exercise, OR a mock disaster drill, OR a tabletop exercise or workshop. Analyze and maintain documentation of all drills, tabletop exercises, and emergency events, and revise the emergency plan, as needed. AAAHC requires a second exercise each year. This may be a second full-scale exercise that is community-based, or an individual, facility-based functional exercise, OR a mock disaster drill, OR a tabletop exercise. | Facility Personnel | A or 2A | [12 empty] | Safety section 2 or 3 – Disaster Safety
Emergency Call Light Test | Complete Form: Emergency Call System Inventory and Annual Testing. | Trained Facility Personnel | A
Emergency Generator Testing | Obtain report of operating the generator for 90 minutes under full load. A full-service inspection may need to be performed including lubrication, cooling system, air induction and exhaust system, battery system, belts and running checks (Check your manufacturer’s guidelines and discuss with your ancillary contracted vendor). Must include a Generator Fuel Testing. Keep with contract for annual evaluation. NOTE: The annual generator run for 90-Minutes is ONLY required, if in the previous twelve months the generator could not or did not for whatever reason meet the minimum 30% load of the nameplate rating or minimum exhaust gas temperature as recommended by the manufacturer. | Generator Vendor | A
Emergency Lighting | Perform a functional test of all battery-powered lights required for egress for a duration of 1.5 hours. Create a log and keep documentation of this. This must include documentation of the emergency lighting in the OR. | Trained Facility Personnel | A | [12 empty] | Safety section 3 or 4 - Safety Management
Fire Extinguisher Preventative Maintenance | Obtain report of required ITM from your ancillary contracted vendor. Keep with contract for annual evaluation | Fire Extinguisher Vendor | A
Fire/Smoke/Automatic Sprinkler Alarm System Testing and Maintenance | Obtain reports for required ITMs from your ancillary contracted vendor. Keep with contract for annual evaluation. | Fire Sprinkler Vendor | A
HVAC Inspection and Service | Obtain reports for required ITMs from your ancillary contracted vendor. Keep with contract for annual evaluation. | HVAC Vendor | A
Air Exchanges and Air Pressure Checks | Obtain report of required ITM from your ancillary contracted vendor. Keep with contract for annual evaluation. | Air Balancing Vendor | A | [12 empty] | Nursing section 2
Medical Gas System and Vaccuum Pump | Obtain reports for required ITMs from your ancillary contracted vendor. Keep with contract for annual evaluation. | Medical Gas Vendor | A
Line Isolation Monitoring | If applicable. For a LIM circuit with automated self-test and self-calibration capabilities, this test shall be performed at intervals of not more than 12 months. Actuation of the test switch shall activate both the visual and audible alarm indicators. Obtain reports for required ITM from vendor. | Certified Electrical Vendor | A | [12 empty] | Safety section 3 or 4 - Safety Management
Receptacles | Hospital-grade receptacles must be tested after initial installation, replacement, or servicing. Non-hospital grade at patient bed locations and in locations where deep sedation or general anesthesia is administered must be tested annually. Log visual inspection, continuity of grounding circuit, polarity of connections, retention force of grounding blade. | Certified Electrical Vendor | A
Safety Management Plan Risk Assessments (TJC facilities only) | Develop/update and review the following risk assessments to be used in conjunction with safety management plans: Safety and Security, Fire, Hazardous Materials and Waste, Medical Equipment and Utilities. For TJC accredited facilities only. | Facility Personnel | A | [12 empty] | Safety section 1
Emergency Generator | Obtain report for 4 hour load testing. Check with your ancillary contracted vendor for load bank percentages. Keep with contract for annual evaluation | Generator Vendor | 3
Smoke and Fire Damper Test | Obtain report of physical inspection by trained and certified vendor. | Trained and Certified Vendor | 4
Sprinkler System Inspection and Testing | Gauges tested or replaced, sprinkler pressure-reducing valve: full flow test compared to previous test results. Alarm and check valve, obtruction, and backflow inspection. Obtain reports from certified vendor. | Trained and Certified Vendor | 5
Biomed Equipment Check | Biomed inspection and safety check on all electric patient care equipment in facility. ITM schedule is based on documented risk assessment. Keep with contract for annual evaluation. | Bio-Med Vendor and Facility Personnel | V
Equipment Preventative Maintenance | Obtain documentation of PM performed on equipment per manufacturer’s guidelines. This pertains to all equipment including, but not limited to anesthesia machines, autoclaves, C-arms, lasers, microscopes, etc. Keep with contract for annual evaluation. | Bio-Med Vendor | V
Wet/Dry Locations Risk Assessment | Conduct a wet/dry locations risk assessment. Report to QAPI/MAC/GB. Update/revise when any revisions are made to facility Scope of Care. | Facility Personnel | V
Sprinkler System | Every 10 years - dry head sprinkler replacement, 20 years - quick response (QR) sprinkler head replacement, 50 years - standard response (SR) sprinkler head replacement | Trained and Certified Vendor | V
W = Weekly
M = Monthly
Q = Quarterly
A = Annually
2A = Twice per year
4 = every 4 years
5 = every 5 years
V = variable (per manufacturer or facilty needs)

## LSC DAILY REQUIREMENTS
ASC OPERATIONAL COMPLIANCE CALENDAR
DAILY REQUIREMENTS
REQUIREMENT | DOCUMENTATION | FREQUENCY | WHO IS RESPONSIBLE | PSS P&P REFERENCE
Fire Safety | Ensure exit pathway, lines of egress, fire extinguishers, and fire alarm pull stations are unobstructed. Ensure fire-rated doors and self-closing doors latch and aren't damaged. Track on a log. | D | Trained Facility Personnel
Medical Gas | Ensure a reserve supply of at least two cylinders is connected to the manifold. Track on a log. | D | Trained Facility Personnel | Safety section 3 or 4 - Safety Management
Temperature and Humidity | Log temperature and humidity, including action and resolution if the temperature or humidity are out of range. Operating Room (Class B and C) Temperature range 68 – 75°F Humidity range 20 – 60% Procedure Room (Class A) Temperature range 70 – 75°F Humidity range 20 – 60% Clean Utility (Clean Workroom) Temperature range 68 – 73°F Humidity maximum of 60% Sterile Storage Temperature maximum of 75°F Humidity maximum of 60% Soiled Utility (Decontamination Room) Temperature range 60 – 73°F PACU Temperature range 70 – 75°F Humidity range 20 – 60% | D | Trained Facility Personnel | Nursing section 2
Medical Device Malfunction (Mandatory) | Report deaths, serious illnesses or injuries caused by a medical device to the FDA and/or manufacturer per regulatory standard. | D I/A/O | Trained Facility Personnel/Vendor | Safety section 4 or 5 – Equipment Safety
D = Daily
D I/A/O = Daily if applicable and/or with occurrence